{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":12,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWS-J-SS"]
[]
[]
[]
[]
["","","","","","EWWS120J-SS","EWWS140J-SS","EWWS150J-SS","EWWS180J-SS","EWWS210J-SS","EWWS240J-SS","EWWS270J-SS"]
["Απόδοση ψύξης","Ονομ.","","","kW","115.2","136.3","154.7","180.6","207.3","241","272.2"]
["Έλεγχος απόδοσης","Μέθοδος","","","","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless"]
["","Ελάχιστη απόδοση","","","%","25","25","25","25","25","25","25"]
["Ισχύς εισόδου","Ψύξη","","Ονομ.","kW","30","36.3","41.7","47.8","54.2","65.7","74.4"]
["EER","","","","","3.85","3.75","3.72","3.78","3.82","3.67","3.66"]
["IPLV","","","","","4.1","4.11","4.09","4.11","4.12","4.64","4.59"]
["SEER","","","","","3.36","3.38","3.32","3.4","3.39","3.87","3.82"]
["Διαστάσεις","Μονάδα","","Βάθος","mm","2684","2684","2684","2684","2684","2684","2684"]
["","","","Ύψος","mm","1020","1020","1020","1020","1020","1020","1020"]
["","","","Πλάτος","mm","913","913","913","913","913","913","913"]
["Βάρος","Βάρος λειτουργίας","","","kg","1211","1276","1378","1415","1473","1663","1675"]
["","Μονάδα","","","kg","1177","1233","1334","1366","1416","1600","1607"]
["Περίβλημα","Χρώμα","","","","Κρεμ","Κρεμ","Κρεμ","Κρεμ","Κρεμ","Κρεμ","Κρεμ"]
["","Υλικό","","","","Γαλβανισμένο και βαμμένο χαλυβδοέλασμα","Γαλβανισμένο και βαμμένο χαλυβδοέλασμα","Γαλβανισμένο και βαμμένο χαλυβδοέλασμα","Γαλβανισμένο και βαμμένο χαλυβδοέλασμα","Γαλβανισμένο και βαμμένο χαλυβδοέλασμα","Γαλβανισμένο και βαμμένο χαλυβδοέλασμα","Γαλβανισμένο και βαμμένο χαλυβδοέλασμα"]
["Εναλλάκτης θερμότητας νερού - εξατμιστής","Τύπος","","","","Εναλλάκτης θερμότητας πλάκας","Εναλλάκτης θερμότητας πλάκας","Εναλλάκτης θερμότητας πλάκας","Εναλλάκτης θερμότητας πλάκας","Εναλλάκτης θερμότητας πλάκας","Εναλλάκτης θερμότητας πλάκας","Εναλλάκτης θερμότητας πλάκας"]
["","Όγκος νερού","","","l","14","18","14","17","20","26","26"]
["Εναλλάκτης θερμότητας νερού - εξατμιστήρας","Πτώση πίεσης νερού","Ψύξη","Ονομ.","kPa","17.1","16.8","32.8","33.4","31.8","27.9","34.8"]
["Συμπιεστής","Ποσότητα","","","","1","1","1","1","1","1","1"]
["","Τύπος","","","","Κοχλιοφόρος (single screw) συμπιεστής","Κοχλιοφόρος (single screw) συμπιεστής","Κοχλιοφόρος (single screw) συμπιεστής","Κοχλιοφόρος (single screw) συμπιεστής","Κοχλιοφόρος (single screw) συμπιεστής","Κοχλιοφόρος (single screw) συμπιεστής","Κοχλιοφόρος (single screw) συμπιεστής"]
["Εύρος λειτουργίας","Πλευρά νερού","Εξατμιστής","Ελάχ.","°CDB","-10","-10","-10","-10","-10","-10","-10"]
["","","","Μέγ.","°CDB","15","15","15","15","15","15","15"]
["Στάθμη ηχητικής ισχύος","Ψύξη","","Ονομ.","dBA","95","95","95","95","95","95","95"]
["Στάθμη ηχητικής πίεσης","Ψύξη","","Ονομ.","dBA","79","79","79","79","79","79","79"]
["Ψυκτικό μέσο","Τύπος","","","","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A"]
["","GWP","","","","629.5","629.5","629.5","629.5","629.5","629.5","629.5"]
["","Φορτίο","","","kg","18","35","34","37","37","38","38"]
["","Κυκλώματα","","Ψυκτικό μέσο-=-Κυκλώματα-=-Ποσότητα","","1","1","1","1","1","1","1"]
["Συνδέσεις σωληνώσεων","Είσοδος/έξοδος νερού εξατμιστή (Εξ. Διάμ.)","","","","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm"]
["Εύρος ενεργειακής αποδοτικότητας","","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F"]
["Τροφοδοσία ισχύος","Φάση","","","","3~","3~","3~","3~","3~","3~","3~"]
["","Συχνότητα","","","Hz","50","50","50","50","50","50","50"]
["","Τάση","","","V","400","400","400","400","400","400","400"]
["","Εύρος τάσης","","Ελάχ.","%","-10","-10","-10","-10","-10","-10","-10"]
["","","","Μέγ.","%","10","10","10","10","10","10","10"]
["Μονάδα","Ρεύμα εκκίν.","","Μέγ.","A","154","154","198","198","198","291","291"]
["","Ρεύμα λειτ.","Ψύξη","Ονομ.","A","50","60","70","78","87","105","117"]
["","","","Μέγ.","A","81","96","108","122","141","164","185"]
["","Μέγ. ένταση ρεύματος μονάδας για μέγεθος των καλωδίων","","","A","89","107","120","136","158","183","207"]
["Σημειώσεις","","","","","(1) - Ψύξη: EW 12°C; LW 7°C; συνθήκες περιβάλλοντος: 35°CDB","(1) - Ψύξη: EW 12°C; LW 7°C; συνθήκες περιβάλλοντος: 35°CDB","(1) - Ψύξη: EW 12°C; LW 7°C; συνθήκες περιβάλλοντος: 35°CDB","(1) - Ψύξη: EW 12°C; LW 7°C; συνθήκες περιβάλλοντος: 35°CDB","(1) - Ψύξη: EW 12°C; LW 7°C; συνθήκες περιβάλλοντος: 35°CDB","(1) - Ψύξη: EW 12°C; LW 7°C; συνθήκες περιβάλλοντος: 35°CDB","(1) - Ψύξη: EW 12°C; LW 7°C; συνθήκες περιβάλλοντος: 35°CDB"]
["","","","","","(2) - Ψύξη: EW 23°C; LW 18°C; συνθήκες περιβάλλοντος: 35°CDB","(2) - Ψύξη: EW 23°C; LW 18°C; συνθήκες περιβάλλοντος: 35°CDB","(2) - Ψύξη: EW 23°C; LW 18°C; συνθήκες περιβάλλοντος: 35°CDB","(2) - Ψύξη: EW 23°C; LW 18°C; συνθήκες περιβάλλοντος: 35°CDB","(2) - Ψύξη: EW 23°C; LW 18°C; συνθήκες περιβάλλοντος: 35°CDB","(2) - Ψύξη: EW 23°C; LW 18°C; συνθήκες περιβάλλοντος: 35°CDB","(2) - Ψύξη: EW 23°C; LW 18°C; συνθήκες περιβάλλοντος: 35°CDB"]
["","","","","","(3) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - Κατά EN14825","(5) - Κατά EN14825","(5) - Κατά EN14825","(5) - Κατά EN14825","(5) - Κατά EN14825","(5) - Κατά EN14825","(5) - Κατά EN14825"]
["","","","","","(6) - Εξαρτάται από την κατάσταση λειτουργίας,  συμβουλευθείτε το εγχειρίδιο εγκατάστασης.","(6) - Εξαρτάται από την κατάσταση λειτουργίας,  συμβουλευθείτε το εγχειρίδιο εγκατάστασης.","(6) - Εξαρτάται από την κατάσταση λειτουργίας,  συμβουλευθείτε το εγχειρίδιο εγκατάστασης.","(6) - Εξαρτάται από την κατάσταση λειτουργίας,  συμβουλευθείτε το εγχειρίδιο εγκατάστασης.","(6) - Εξαρτάται από την κατάσταση λειτουργίας,  συμβουλευθείτε το εγχειρίδιο εγκατάστασης.","(6) - Εξαρτάται από την κατάσταση λειτουργίας,  συμβουλευθείτε το εγχειρίδιο εγκατάστασης.","(6) - Εξαρτάται από την κατάσταση λειτουργίας,  συμβουλευθείτε το εγχειρίδιο εγκατάστασης."]
["","","","","","(7) - Για περισσότερες λεπτομέρειες, δείτε το σχέδιο εύρους λειτουργίας","(7) - Για περισσότερες λεπτομέρειες, δείτε το σχέδιο εύρους λειτουργίας","(7) - Για περισσότερες λεπτομέρειες, δείτε το σχέδιο εύρους λειτουργίας","(7) - Για περισσότερες λεπτομέρειες, δείτε το σχέδιο εύρους λειτουργίας","(7) - Για περισσότερες λεπτομέρειες, δείτε το σχέδιο εύρους λειτουργίας","(7) - Για περισσότερες λεπτομέρειες, δείτε το σχέδιο εύρους λειτουργίας","(7) - Για περισσότερες λεπτομέρειες, δείτε το σχέδιο εύρους λειτουργίας"]