{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":61,"n_cols":12,"rows_kept":61,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FCAG-B"]
[]
[]
[]
[]
["","","","","","FCAG35BVEB","FCAG50BVEB","FCAG60BVEB","FCAG71BVEB","FCAG100BVEB","FCAG125BVEB","FCAG140BVEB"]
["Απόδοση ψύξης","Συνολική απόδοση","","Ονομ.","kW","3.50","5.00","5.70","6.80","9.50","12.10","13.40"]
["Απόδοση σε λειτουργία θέρμανσης","Συνολική απόδοση","","Ονομ.","kW","4.2","6.0","7.0","7.5","10.8","13.5","15.5"]
["Περίβλημα","Υλικό","","","","Γαλβανισμένο χαλυβδοέλασμα","Γαλβανισμένο χαλυβδοέλασμα","Γαλβανισμένο χαλυβδοέλασμα","Γαλβανισμένο χαλυβδοέλασμα","Γαλβανισμένο χαλυβδοέλασμα","Γαλβανισμένο χαλυβδοέλασμα","Γαλβανισμένο χαλυβδοέλασμα"]
["Διαστάσεις","Μονάδα","","Ύψος","mm","204","204","204","204","246","246","246"]
["","","","Πλάτος","mm","840","840","840","840","840","840","840"]
["","","","Βάθος","mm","840","840","840","840","840","840","840"]
["Βάρος","Μονάδα","","","kg","18","19","19","21","23","23","23"]
["Ανεμιστήρας","Ταχύτητα ροής αέρα","Ψύξη","Υψ.","m³/min","12.9","14.6","14.9","15.1","22.7","27.2","27.2"]
["","","","Μέτρια","m³/min","10.6","11.8","12.2","13","17.8","20.4","20.4"]
["","","","Χαμηλή","m³/min","8.8","9.4","9.6","10.8","13","13.1","13.1"]
["","","Θέρμανση","Υψ.","m³/min","14.1","14.6","14.9","15.1","23","27","27"]
["","","","Μέτρια","m³/min","11.6","11.8","12.2","12.9","18.1","20.2","20.2"]
["","","","Χαμηλή","m³/min","9.4","9.4","9.6","10.8","13.2","13","13"]
["Στάθμη ηχητικής ισχύος","Ψύξη","","","dBA","49","49","51","51","54","58","58"]
["","Θέρμανση","","","dBA","49","49","51","51","54","58","58"]
["Στάθμη ηχητικής πίεσης","Ψύξη","","Υψ.","dBA","31","31","33","35","37","41","41"]
["","","","Μέτρια","dBA","29","29","31","31","33","35","35"]
["","","","Χαμηλή","dBA","27","27","28","28","29","29","29"]
["","Θέρμανση","","Υψ.","dBA","31","31","33","33","37","41","41"]
["","","","Μέτρια","dBA","29","29","31","31","33","35","35"]
["","","","Χαμηλή","dBA","27","27","28","28","29","29","29"]
["Συνδέσεις σωληνώσεων","Υγρό","","ΕΞ.ΔΙΑΜ.","mm","6.35","6.35","6.35","9.52","9.52","9.52","9.52"]
["","Αέριο","","ΕΞ.ΔΙΑΜ.","mm","9.52","12.7","12.7","15.9","15.9","15.9","15.9"]
["","Αποχέτευση","","","","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)"]
["Διακοσμητική μάσκα","Μοντέλο","","","","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B","BYCQ140E2W1, BYCQ140E2W1W, BYCQ140E2W1B"]
["","Διαστάσεις","","Ύψος","mm","65","65","65","65","65","65","65"]
["","","","Πλάτος","mm","950","950","950","950","950","950","950"]
["","","","Βάθος","mm","950","950","950","950","950","950","950"]
["","Βάρος","","","kg","5.5","5.5","5.5","5.5","5.5","5.5","5.5"]
["Διακοσμητική μάσκα 2","Μοντέλο","","","","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B","BYCQ140E2GFW1, BYCQ140E2GFW1B"]
["","Διαστάσεις","","Ύψος","mm","148","148","148","148","148","148","148"]
["","","","Διακοσμητική μάσκα 2-=-Διαστάσεις-=-Πλάτος-=-mm","mm","950","950","950","950","950","950","950"]
["","","","Διακοσμητική μάσκα 2-=-Διαστάσεις-=-Βάθος-=-mm","mm","950","950","950","950","950","950","950"]
["","Βάρος","","","kg","10.3","10.3","10.3","10.3","10.3","10.3","10.3"]
["Διακοσμητική μάσκα 3","Μοντέλο","","","","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB","BYCQ140E2P, BYCQ140E2PB"]
["","Διαστάσεις","","Διακοσμητική μάσκα 3-=-Διαστάσεις-=-Ύψος-=-mm","mm","106","106","106","106","106","106","106"]
["","","","Διακοσμητική μάσκα 3-=-Διαστάσεις-=-Πλάτος-=-mm","mm","950","950","950","950","950","950","950"]
["","","","Διακοσμητική μάσκα 3-=-Διαστάσεις-=-Βάθος-=-mm","mm","950","950","950","950","950","950","950"]
["","Βάρος","","","kg","6.5","6.5","6.5","6.5","6.5","6.5","6.5"]
["Χειριστήρια","Τηλεχειριστήριο υπερύθρων","","","","BRC7FA532F, BRC7FB532F, BRC7FA532FB, BRC7FB532FB","BRC7FA532F, BRC7FB532F, BRC7FA532FB, BRC7FB532FB","BRC7FA532F, BRC7FB532F, BRC7FA532FB, BRC7FB532FB","BRC7FA532F, BRC7FB532F, BRC7FA532FB, BRC7FB532FB","BRC7FA532F, BRC7FB532F, BRC7FA532FB, BRC7FB532FB","BRC7FA532F, BRC7FB532F, BRC7FA532FB, BRC7FB532FB","BRC7FA532F, BRC7FB532F, BRC7FA532FB, BRC7FB532FB"]
["","Τηλεχειριστήριο με καλώδιο","","","","BRC1D528, BRC1E53A7, BRC1E53B7, BRC1E53C7, BRC1H81W/S, BRC1H51(9)W/S/K7, BRC2E52C7, BRC3E52C7","BRC1D528, BRC1E53A7, BRC1E53B7, BRC1E53C7, BRC1H81W/S, BRC1H51(9)W/S/K7, BRC2E52C7, BRC3E52C7","BRC1D528, BRC1E53A7, BRC1E53B7, BRC1E53C7, BRC1H81W/S, BRC1H51(9)W/S/K7, BRC2E52C7, BRC3E52C7","BRC1D528, BRC1E53A7, BRC1E53B7, BRC1E53C7, BRC1H81W/S, BRC1H51(9)W/S/K7, BRC2E52C7, BRC3E52C7","BRC1D528, BRC1E53A7, BRC1E53B7, BRC1E53C7, BRC1H81W/S, BRC1H51(9)W/S/K7, BRC2E52C7, BRC3E52C7","BRC1D528, BRC1E53A7, BRC1E53B7, BRC1E53C7, BRC1H81W/S, BRC1H51(9)W/S/K7, BRC2E52C7, BRC3E52C7","BRC1D528, BRC1E53A7, BRC1E53B7, BRC1E53C7, BRC1H81W/S, BRC1H51(9)W/S/K7, BRC2E52C7, BRC3E52C7"]
["Στάνταρτ εξαρτήματα","Installation manual","","","","1","1","1","1","1","1","1"]
["","Washer for hanger bracket","","","","8","8","8","8","8","8","8"]
["","Operation manual","","","","1","1","1","1","1","1","1"]
["","Wire clamp material","","","","7","7","7","7","7","7","7"]
["","Clamp for drain hose","","","","1","1","1","1","1","1","1"]
["","Clamps","","","","1","1","1","1","1","1","1"]
["","Drain hose","","","","1","1","1","1","1","1","1"]
["","Installation guide","","","","1","1","1","1","1","1","1"]
["","Insulation for fitting","","","","2","2","2","2","2","2","2"]
["","Screws","","","","4","4","4","4","4","4","4"]
["","Sealing pads","","","","1","1","1","1","1","1","1"]
["Τροφοδοσία ισχύος","Φάση","","","","1~","1~","1~","1~","1~","1~","1~"]
["","Συχνότητα","","","Hz","50/60","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Τάση","","","V","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]